SECTION __________

UNDERGROUND BRINE TANK – NSF Listed

- GENERAL

      - PRINCIPAL WORK IN THIS SECTION

        - Brine Tank for underground installation, single or double wall, horizontal, cylindrical, fiberglass tank, compatible with salt, salt brine, and potable water products.  All components shall meet NSF61 requirements and the briner shall bear the NSF61 label.

      - QUALITY ASSURANCE

        - Refer to Section _______:  General Provisions for Plumbing Work.

        - Reference Standards:

- Tank manufacturer shall be listed by NSF under NSF/ANSI Standard 61 Drinking Water System Components – Health Effects

- Tank manufacturer shall be in the business of manufacturing tanks with materials conforming to the requirements of ANSI/AWWA D120-02 Thermosetting Fiberglass-Reinforced Plastic Tanks

- Tank manufacturer shall be in the business of manufacturing tanks to UL 1316 standards

- American Society for Testing and Materials (ASTM) Standards ASTM D883: Standard Terminology Related to Plastics

- U.L. - Underwriters Laboratories, Inc

      - SUBMITTALS

        - Submit product data, drawings, and test reports for the following items per the provisions of Division 1 and this division's General Provisions:

- The manufacturer shall submit a complete set of scale shop drawings detailing dimensions of heights, diameter, elevations to invert, pipe sizes, pipe connections, fittings and other appurtenances

- Catalog data

- Manufacturer’s installation instructions

- PRODUCTS

      - MANUFACTURERS

        - Underground Brine Tanks:

- BrineMaker, Inc. 800-998-7345

- Or approved equal

        - Underground briner supplier shall have provide documentation of testing conducted to demonstrate the effectiveness of their salt distribution system design for briners exceeding 10’ in length

        - Underground briner supplier shall be regularly engaged in the design and engineering of underground fiberglass briners and upon request, shall provide a list of installations including the system OEM and end user contact name(s) and phone number(s)

      - FIBERGLASS UNDERGROUND NSF LISTED STORAGE TANK                                         (listed for Potable Water)

        - Loading Conditions – The brine tank shall meet the following design criteria:

- Internal Load – All brine tanks shall be testable and shall withstand a 5-psig air-pressure test with 5:1 safety factor. Maximum test pressure is 5 psig

- Surface Loads – brine tank shall withstand surface H-20 and HS-20 axle loads when properly installed according to manufacturers current Installation Manual and Operating Guidelines

- External Hydrostatic Pressure and Burial Depth – tank shall be capable of being buried in ground with 7' of overburden over the top of the tank, the hole fully flooded, and maintain a safety factor of 5:1 against general buckling

- The brine tank shall support accessory equipment – such as manways, manway extensions, collar/ risers, FRP inlet/outlet piping, baffle wall, anti-vortex plates and pump platforms when installed according to tank manufacturers current Installation Manual and Operating Guidelines

- Buried tanks shall be manufactured with integral trapezoidal ribs for structural integrity

        - Product Storage

- Tank shall be capable of handling liquids with specific gravity up to 1.3

- Tank shall be vented to atmospheric utilizing a dust bag to capture salt dust while having sufficient surface area and fabric design to prevent over-pressurization of the briner

- Tank shall be capable of handling salt brine at ambient temperature

        - Materials

- Tank shall be manufactured with 100% premium resin (Terephthalic polyester or highly cross-linked Isophthalic polyester resins for the exterior and NSF Listed resin for the interior only), and chopped glass.  No fillers or extenders shall be used.  No General, Orthophthalic, or odd lot resin shall be used

- All associated internal mounting hardware shall be rustproof

- All exposed internal FRP components to be constructed using NSF listed materials

- All materials used in the construction of the vessel and appurtenances shall be compatible with salt brine

        - Interstitial Space for Double-Wall Application

- Tank shall have a space between the primary and secondary walls to allow for the free flow and containment of leaked product from the primary tank. The space also allows the insertion of a monitoring device through a monitoring fitting

- Each interstitial space monitor fitting shall consist of a 4" NPT fitting

        - Vessel shall be post cured to meet NSF requirements and shall bear the NSF61 label

      - Standard features

        - Manway Opening

- Provide at least one 30” flanged manway opening with extension to grade with watertight cover

- When an internal ladder is provided, a section of ladder shall be integral to the extension

- B.	Standard Connections

- Water Inlet:  	2” flange / 1” coupling with 1” interior SS water distribution header system

- Brine Outlet:	3” flange withv 2” internal collection plenum and check valve

- Level Sensor:	3” flange with internal stilling well and support

- Vent:		8” flange and flanged extension to grade + dust bag + SS clamps

- Salt  Inlet:	6” flange  x 4” SS header + 4” SS flanged extension to grade + quick connect and cap – and with an internal SS distribution header (for even salt distribution throughout vessel)

        - Fitting Enclosures

- (2) 42” diameter x 36” tall (other heights available depending on burial depth) enclosures shall be provided for the connections as identified in section B above

- Enclosure shall be cut to length and bonded in the field - by others

        - Lifting Lugs

- All Tanks shall have lifting lugs that are capable of withstanding weight of tank with a safety factor of at least 2:1

      - options

        - Water Level Control System

- The Water Level Control System shall consist of a submersible pressure transmitter, controller with LED readout, relays, and 4-20mA repeater, NEMA 4X enclosure, and solenoid valve

        - Salt Level Indication System

- The Salt Level Indication System shall consist of a Brine Concentration Monitoring System with installation TEE, submersible torroidal conductivity sensor with 4-20mA signal, controller with LED readout, relays, and 4-20mA repeater

        - Ladder

- FRP ladder(s) shall be NSF Listed under ANSI/NSF Standard 61 as supplied by tank manufacturer

- Manway extension to grade shall include a ladder section

        - Dust Bag Housing

- Protect the dust bag from the elements and the briner from over-pressurization

        - NSF 61/ANSI Labeled

- Certified to NSF 61/ANSI (for potable water)

        - Gravel Bed

- The brine collection plenum shall be covered by 7” of 1/4” – 1/2” and then 5” of 1/8” – 1/4” NSF/AWWA quartz stone to serve as a filtration layer (as recommended by Morton Salt)

        - Traffic Covers - 3

- (3) H25 rated fiberglass traffic covers for grade access to fitting housings and manway

        - Complete Anchorage System

- The Complete Anchorage System shall consist of precast concrete deadmen, fiberglass straps, and turnbuckles

        - Day Tanks

- Fully equipped HDPE Day Tank including inlet, outlet, drain, level, vent, manway and restraint system in 540, 1,090, 1,550, or 2,500, or 4,925 gallons capacity.

- 2.5 	PERFORMANCE

- Salt Distribution:  Salt shall be distributed evenly throughout the briner via a roof mounted stainless steel distribution header such that there is one connection point for the delivery truck.  Briner manufacturer shall have conducted salt distibution testing to verify and demonstrate the effectiveness of the distribution system.  Distribution header shall be supported as necessary to prevent damage during transit, offloading, and installation.

- Water Inlet:  Water shall be distributed evenly throughout the briner via a roof mounted stainless steel distribution header such that there is one connection point.  Distribution header shall be supported as necessary to prevent damage during transit, offloading, and installation.

- Brine Collection:  Brine shall be evenly collected from the briner via a collection plenum whose length shall be no less that the shell length of the briner – brackets shall be spaced <48” apart.  Connecting piping to the roof mounted connection flange shall be bracketed to the side shell of the briner in 4 (min) equally spaced locations.  Connecting piping shall include a check valve.

- Vent:  Vent connection shall be 8”.  A dust bag shall be included and designed to capture >1 micron particles with 90% efficiency and shall be sized to provide sufficient venting to prevent over-pressurization of the briner.

- eXECUTION

      - INSTALLATION

        - Tank shall be installed according to the Manufacturer's Installation Manual and Operating Guidelines for Underground Brine Tanks

      - TESTS

        - Tank shall be tested according to the Manufacturer's Installation Manual and Operating Guidelines for Underground Brine Tanks

- warranty

        - Briner vessel shall be warranteed for one year

        - Salt fill line shall be warranteed for five years

        - Dust bag shall be warranteed for 90 days

        - Electronics shall be warranteed per manufacturer’s standard

        - Ladder shall be warranteed for one year

END OF SECTION